## List of Service Requests
Service Request | Summary | Location | Asset | Priority | Reported By | Reported Date | inbox | WO# | Status | History | Site
SR-74612 | Leaking flange | EJ-1837 | 2563 | 4 | JORDAN.GILBERT | 2025-11-25 16:11 | AARON.HUNTER |  | QUEUED | N | CHATHAM
SR-74548 | Vib25 - Balance Fan Wheel | BL-1829 | 10034 | 4 | JORDAN.GILBERT | 2025-11-21 12:00 | AARON.HUNTER |  | QUEUED | N | CHATHAM
SR-73828 | Air flow measurement on inlet duct to dryer A cooler | E-1834 | 2561 | 4 | DAVIN.KENDRICK | 2025-10-07 13:12 |  | 25-53363 | INPROG | N | CHATHAM
SR-73602 | MOC25-052 - Reclassification of Cooler Louver Timer from Tuning Parameters to Operating Parameters | E-1834 | 2561 | 1 | MOHAMMED.MOUSA | 2025-09-24 11:55 |  |  | CLOSED | Y | CHATHAM
SR-73379 | TA25 Vib 25 - BL-1829 Change Bearing/Clean Fan Wheel | BL-1829 | 10034 | 4 | JORDAN.GILBERT | 2025-09-09 07:47 |  | 25-51677 | INPROG | N | CHATHAM
SR-73334 | TA25 Fall P-1837 is leaking... again. | P-1837 |  | 4 | JORDAN.GILBERT | 2025-09-04 17:38 |  | 25-51560 | RESOLVED | N | CHATHAM
SR-73143 | Rebuild RV for spare | RV-1834 |  | 4 | KRIS.QUAGLIOTTO | 2025-08-25 08:12 |  | 25-50535 | QUEUED | N | CHATHAM
SR-72760 | Change DE pillow block bearing BL-1829 | BL-1829 | 10034 | 4 | JORDAN.GILBERT | 2025-08-01 10:01 |  | 25-48941 | RESOLVED | N | CHATHAM
SR-72287 | Install and Wire interposing relay on cooler Damper controls | E-1834 | 2561 | 4 | KEITH.LIBBRECHT | 2025-07-03 09:33 |  | 25-44865 | CLOSED | Y | CHATHAM
SR-72277 | DRO - Rubbing Noise Coming from RV-1834 | RV-1834 |  | 1 | JORDAN.GILBERT | 2025-07-02 17:59 |  | 25-45192 | CLOSED | Y | CHATHAM
SR-72150 | I/E Clean FT18110/18111 -Dryer A Combustion Air flow transmitters | FT-18110 | 3611 | 1 | MANDY.YOUNG | 2025-06-25 07:48 |  | 25-44410 | CLOSED | Y | CHATHAM
SR-71930 | DROA DC-1834 Bag should be changed | DC-1834 |  | 4 | BRAD.TINLINE | 2025-06-12 09:45 |  | 25-43509 | RESOLVED | N | CHATHAM
SR-71927 | DRO - DC-1834 Replace all couplers on pulser tube | DC-1834 |  | 4 | BRAD.TINLINE | 2025-06-12 08:54 |  | 25-43510 | RESOLVED | N | CHATHAM
SR-71926 | DRO DC1834 Had product , and standing water on clear air side | DC-1834 |  | 4 | BRAD.TINLINE | 2025-06-12 08:22 |  | 25-43511 | RESOLVED | N | CHATHAM
SR-71870 | Inspect Air Pulsers and Bags DC-1834 | DC-1834 |  | 1 | JORDAN.GILBERT | 2025-06-09 16:08 |  | 25-43456 | CLOSED | Y | CHATHAM
SR-71855 | P-1837 leaking at stem- review design (repeat failure) | P-1837 |  | 4 | FRANCIS.UMOH | 2025-06-08 22:53 | MICHAEL.JACOBSON | 23-34156 | NEW | N | CHATHAM
SR-71624 | DRO Modify Knee Brace E-1834 | E-1834 | 2561 | 4 | JORDAN.GILBERT | 2025-05-26 11:31 |  | 25-43523 | RESOLVED | N | CHATHAM
SR-71507 | SS nuts have to be cut off all bolt holes on door flange | XV-18174A | 6891 | 1 | BRAD.TINLINE | 2025-05-20 08:10 |  | 25-50886 | INPROG | N | CHATHAM
SR-71506 | SS nuts have to be cut off all bolt holes on door flange | XV-18176A | 6400 | 1 | BRAD.TINLINE | 2025-05-20 07:58 |  | 25-50884 | INPROG | N | CHATHAM
SR-71412 | TA25 Spring found work - Cyclone pop door limit switch not working | XV-18174B | 6399 | 1 | SCOTT.GALLANT | 2025-05-13 08:36 |  | 25-41088 | CLOSED | Y | CHATHAM
SR-71284 | DRO - Modify S/S 2" pipe and re-plumb joints | EJ-1837 | 2563 | 4 | TAYLOR.LINDSAY | 2025-05-07 08:52 |  | 25-41148 | RESOLVED | N | CHATHAM
SR-71118 | DRO TA25 Spring Taco Pump seal is leaking | P-1837 |  | 4 | JORDAN.GILBERT | 2025-04-28 09:57 |  | 25-39945 | CLOSED | Y | CHATHAM
SR-70718 | Packing Gland Has come unbolted CV-1828 | CV-1828 |  | 1 | JORDAN.GILBERT | 2025-04-03 17:19 |  | 25-37365 | CLOSED | Y | CHATHAM
SR-70682 | MOC25-033 Cyclone Pop Door Jumper Continuation | XV-18176A | 6400 | 4 | MICHAEL.JACOBSON | 2025-04-02 12:36 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-70651 | TA25 Spring - I/E and IMF Pop Door switches rework | XV-18176A | 6400 | 4 | VIRAJ.PATEL | 2025-04-01 11:30 |  | 25-37331 | CLOSED | Y | CHATHAM
SR-70548 | Adjusting TP35 | E-1834B | 2562 | 1 | MOHAMMED.MOUSA | 2025-03-25 16:50 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-70528 | DROA TA25 Spring - Repair leaks on pick heater system for turbo tak | EJ-1837 | 2563 | 4 | JORDAN.GILBERT | 2025-03-25 07:58 |  | 25-37332 | CLOSED | Y | CHATHAM
SR-70470 | LT-41310 (Dryer A sump) is showing bad I/O | LT-41310 | 3686 | 4 | JOSHUA.HOORELBECK | 2025-03-22 01:50 |  | 25-36358 | CLOSED | Y | CHATHAM
SR-70427 | XV18174/7 Jumper Log for open limits | XV-18176A | 6400 | 4 | VIRAJ.PATEL | 2025-03-20 11:53 | VIRAJ.PATEL |  | NEW | N | CHATHAM
SR-70404 | South Dryer A Cyclone Pop Door not Reaching Limit | XV-18176B |  | 1 | CODY.STANFORD | 2025-03-19 22:29 |  | 25-35821 | CLOSED | Y | CHATHAM
SR-70390 | Verify DC-1834 air pucks - I&E | DC-1834 |  | 1 | MANDY.YOUNG | 2025-03-19 09:06 |  | 25-35790 | CLOSED | Y | CHATHAM
SR-70389 | DROA - I/E Clean FT18110 -Dryer A Combustion Air flow transmitters | FT-18110 | 3611 | 1 | MANDY.YOUNG | 2025-03-19 09:04 |  | 25-35793 | CLOSED | Y | CHATHAM
SR-70349 | Replace bonding jumpers on BL-1829 inlet and discharge boots | BL-1829 | 10034 | 1 | AARON.HUNTER | 2025-03-17 15:33 |  | 25-35775 | CLOSED | Y | CHATHAM
SR-70043 | Vib25 - Grease Motor BL-1829 | BL-1829 | 10034 | 4 | JORDAN.GILBERT | 2025-03-01 12:43 |  | 25-34342 | CLOSED | Y | CHATHAM
SR-69578 | Millwright - Remove Pop Doors XV18176 | XV-18176A | 6400 | 1 | VIRAJ.PATEL | 2025-02-05 10:38 |  | 25-31763 | CLOSED | Y | CHATHAM
SR-69576 | Millwright - Remove Pop Doors XV18174 | XV-18174A | 6891 | 1 | VIRAJ.PATEL | 2025-02-05 10:32 |  | 25-31767 | CLOSED | Y | CHATHAM
SR-69533 | Dryer A- please remove transmittter prior to HPW feb 5th 2025 | FT-18111 | 3612 | 4 | TYLER.SKINNER | 2025-02-03 15:26 |  | 25-31730 | CLOSED | Y | CHATHAM
SR-69532 | Dryer A-remove transmitter prior to HPW Weds feb 5th | FT-18110 | 3611 | 4 | TYLER.SKINNER | 2025-02-03 15:19 |  | 25-31732 | CLOSED | Y | CHATHAM
SR-69462 | Dryer A repair- ssytem frozen EJ needs thawed inspected and service as required | EJ-1837 | 2563 | 4 | TYLER.SKINNER | 2025-01-30 13:56 |  | 25-31717 | CLOSED | Y | CHATHAM
SR-69461 | Dryer A repair- system frozen needs thawed PM and verified | P-1837 |  | 4 | TYLER.SKINNER | 2025-01-30 13:52 |  | 25-31726 | CLOSED | Y | CHATHAM
SR-69412 | Dryer A repair- HPW BL-1829 | BL-1829 | 10034 | 4 | TYLER.SKINNER | 2025-01-28 16:38 |  | 25-31328 | CLOSED | Y | CHATHAM
SR-69408 | Dryer A Repair - E-1834 Scrape Walls to remove buildup | E-1834 | 2561 | 4 | MICHAEL.JACOBSON | 2025-01-28 14:57 |  | 25-31330 | CLOSED | Y | CHATHAM
SR-69403 | Dryer A Repair - Inspect and Replace Dryer Pop Door Seals and PM actuators | XV-18176A | 6400 | 1 | DAVIN.KENDRICK | 2025-01-28 13:41 |  | 25-31333 | CLOSED | Y | CHATHAM
SR-69401 | Dryer A Repair - Inspect and Replace Dryer Pop Door Seal and PM actuator | XV-18174A | 6891 | 1 | DAVIN.KENDRICK | 2025-01-28 13:38 |  | 25-31335 | CLOSED | Y | CHATHAM
SR-69388 | Dryer A repair - change suction and inlet expansion joints | BL-1829 | 10034 | 4 | TYLER.SKINNER | 2025-01-28 12:53 |  | 25-31340 | CLOSED | Y | CHATHAM
SR-68579 | Open Dust 1834 collector and inspect | DC-1834 |  | 1 | JORDAN.GILBERT | 2024-12-16 17:37 |  | 24-27829 | CLOSED | Y | CHATHAM
SR-68564 | I/E Keith L - Rockwell Support for BL1829 Dryer A SD Work | BL-1829 | 2868 | 4 | VIRAJ.PATEL | 2024-12-16 10:33 |  | 24-27823 | CLOSED | Y | CHATHAM
SR-68367 | Dryer A Fan Bearing/Winding Temperature Sensor Review/Fix | BL-1829 |  | 4 | MICHAEL.JACOBSON | 2024-12-03 16:27 |  | 24-26650 | CLOSED | Y | CHATHAM
SR-68245 | Clean and overhaul RV-1834 | RV-1834 |  | 4 | JORDAN.GILBERT | 2024-11-25 15:38 |  | 24-25868 | CLOSED | Y | CHATHAM
SR-67324 | TA24 Fall - REMOVE INSTRUMENTATION ON DC-1834 | DC-1834 | 2537 | 4 | DAVIN.KENDRICK | 2024-09-27 08:31 |  | 24-20020 | CLOSED | Y | CHATHAM
SR-67323 | RIGGING ASSISTANCE FOR DC-1834 REMOVAL AND INSTALL (CONNOR?) | DC-1834 | 2537 | 1 | DAVIN.KENDRICK | 2024-09-27 08:28 |  | 24-20021 | CLOSED | Y | CHATHAM
SR-66874 | Cement blocks appear to have got bumped , So scaffold leg does not look to be positioned properly | CV-1828 |  | 1 | BRAD.TINLINE | 2024-08-28 17:05 |  | 24-18204 | CLOSED | Y | CHATHAM
SR-66852 | Remove RV-1834 Motor and Install on New Unit | RV-1834 |  | 4 | JORDAN.GILBERT | 2024-08-28 10:50 |  | 24-17290 | CLOSED | Y | CHATHAM
SR-66731 | REMOVE INSULATION ON INLET FLANGE FROM E-1834 TO DC-1834 | DC-1834 |  | 1 | DAVIN.KENDRICK | 2024-08-21 13:48 |  | 24-17232 | CLOSED | Y | CHATHAM
SR-66493 | TA 24 Fall-Change bearings on BL-1829 | BL-1829 |  | 4 | TAYLOR.LINDSAY | 2024-08-08 11:33 |  | 24-15763 | CLOSED | Y | CHATHAM
SR-66389 | RV-1834 Design Review - repeat failure | RV-1834 |  | 4 | MANDY.YOUNG | 2024-08-01 12:47 | VIRAJ.PATEL |  | NEW | N | CHATHAM
SR-66367 | RV1834 HH amps | RV-1834 | 2876 | 1 | MANDY.YOUNG | 2024-07-31 12:56 |  | 24-15243 | CLOSED | Y | CHATHAM
SR-66349 | DRO- take down fence for HPW and reinstall after work | BL-1829 |  | 4 | TYLER.SKINNER | 2024-07-31 10:19 |  | 24-15265 | CLOSED | Y | CHATHAM
SR-66335 | DRO - Small hole in DC1834 hopper | DC-1834 |  | 4 | DAN.ENGLISH | 2024-07-31 01:51 |  | 24-15301 | CLOSED | Y | CHATHAM
SR-66303 | DRO - Inspect P1837 seal and PSV | P-1837 |  | 4 | MANDY.YOUNG | 2024-07-30 08:44 |  | 24-15182 | CLOSED | Y | CHATHAM
SR-66262 | TA24 Fall - I/E - Kieth work with Erica F on P1837 testing (2hr) | P-1837 |  | 4 | VIRAJ.PATEL | 2024-07-26 11:13 |  | 24-15178 | CLOSED | Y | CHATHAM
SR-66220 | TA24 Fall- Change drive and driven end bearing and send for analysis | CV-1828 |  | 4 | TYLER.SKINNER | 2024-07-25 10:10 |  | 24-14729 | CLOSED | Y | CHATHAM
SR-66196 | DRO - Repair belt guards on CV-1828 | CV-1828 |  | 4 | BRAD.TINLINE | 2024-07-24 06:01 |  | 24-15133 | CLOSED | Y | CHATHAM
SR-66157 | CV-1828 belt and sheave replace | CV-1828 |  | 1 | BRAD.TINLINE | 2024-07-22 17:17 |  | 24-14571 | CLOSED | Y | CHATHAM
SR-66075 | Failed bearing CV-1828 | CV-1828 |  | 1 | MANDY.YOUNG | 2024-07-18 07:35 |  | 24-14142 | CLOSED | Y | CHATHAM
SR-65569 | Rebuild RV-1834 | RV-1834 | 2876 | 4 | JORDAN.GILBERT | 2024-06-21 14:42 |  | 24-14686 | CLOSED | Y | CHATHAM
SR-65561 | DROA - I/E - Confined Space - XZSC18174 Close Limit | XV-18174B | 6399 | 4 | VIRAJ.PATEL | 2024-06-21 12:20 |  | 24-12489 | CLOSED | Y | CHATHAM
SR-65519 | TA24 Fall - INSTALL REPLACEMENT E-1834 | E-1834 | 2561 | 4 | DAVIN.KENDRICK | 2024-06-20 12:22 |  | 24-12491 | CLOSED | Y | CHATHAM
SR-65490 | DROA - Change out RV-1834 | RV-1834 | 2876 | 1 | JORDAN.GILBERT | 2024-06-19 13:48 |  | 24-12099 | CLOSED | Y | CHATHAM
SR-65472 | RV-1834 Chain Inspection | RV-1834 |  | 1 | JOSH.BURM | 2024-06-19 05:01 |  | 24-12083 | CLOSED | Y | CHATHAM
SR-65356 | TA24 Fall - DROA - BL-1829 Change suction/discharge expansion boots | BL-1829 |  | 4 | JORDAN.GILBERT | 2024-06-13 09:26 |  | 24-12043 | CLOSED | Y | CHATHAM
SR-65239 | RV 1834 is making an unusual noise | RV-1834 | 2876 | 4 | DAN.ENGLISH | 2024-06-06 03:34 |  | 24-11511 | CLOSED | Y | CHATHAM
SR-64542 | (Add) TA24 Spring - Inspect Steam/water strainers for Turbotak System | EJ-1837 | 2563 | 1 | MOHAMMED.MOUSA | 2024-05-02 11:43 |  | 24-12497 | CLOSED | Y | CHATHAM
SR-64513 | TA24 BREAK IN - XV18174 is bypassed and needs calibration. | XV-18174B | 6399 | 1 | VIRAJ.PATEL | 2024-05-01 11:05 |  | 24-8669 | CLOSED | Y | CHATHAM
SR-64332 | Hydraulic pump is not moving the louvres in the DDG cooler | E-1834B | 2562 | 4 | DAN.ENGLISH | 2024-04-20 03:45 |  | 24-8326 | CLOSED | Y | CHATHAM
SR-63337 | DROA - Balance fan wheel BL-1829 | BL-1829 |  | 4 | JORDAN.GILBERT | 2024-02-26 10:47 |  | 24-4802 | CLOSED | Y | CHATHAM
SR-63043 | Repair insulation blankets on DC-1834 hopper | DC-1834 | 2537 | 1 | MANDY.YOUNG | 2024-02-12 07:32 |  | 24-3861 | CLOSED | Y | CHATHAM
SR-62963 | (ADD) TA24 VIB24 - Inspect/Change DE bearing BL-1829 | BL-1829 | 10034 | 1 | JORDAN.GILBERT | 2024-02-09 08:58 |  | 24-3976 | CLOSED | Y | CHATHAM
SR-62860 | DROA - E-1834B Repair/Stop Oil leak at hydraulic unit | E-1834B | 2562 | 4 | SCOTT.GALLANT | 2024-02-04 11:13 |  | 24-3975 | CLOSED | Y | CHATHAM
SR-62806 | TA24 Spring - Internal cleaning of DC-1834 | DC-1834 |  | 4 | MANDY.YOUNG | 2024-02-01 09:36 |  | 24-3315 | CLOSED | Y | CHATHAM
SR-62667 | DROA - Dryer A - Dust collector - BAG CATCH GRID Removal | DC-1834 | 2537 | 1 | MOHAMMED.MOUSA | 2024-01-25 16:47 |  | 24-2493 | CLOSED | Y | CHATHAM
SR-62616 | DROA - I/E Clean FT18110 -Dryer A Combustion Air flow transmitters | FT-18110 | 3611 | 1 | VIRAJ.PATEL | 2024-01-23 09:56 |  | 24-2440 | CLOSED | Y | CHATHAM
SR-62609 | DC-1834 'D' Air Puck Not Cycling | DC-1834 |  | 4 | CHRIS.DYCK | 2024-01-23 04:24 |  | 24-2433 | CLOSED | Y | CHATHAM
SR-62561 | we need a spare pump for P 1837 | P-1837 |  | 4 | BRAD.TINLINE | 2024-01-18 14:53 |  | 24-2503 | CLOSED | Y | CHATHAM
SR-62559 | Steam injection tube is plugged EJ-1837 | EJ-1837 | 2563 | 4 | BRAD.TINLINE | 2024-01-18 14:44 |  | 24-2442 | CLOSED | Y | CHATHAM
SR-62531 | DROA - Change hydraulic oil in cooler | E-1834 | 2561 | 4 | JORDAN.GILBERT | 2024-01-17 10:50 |  | 24-2471 | CLOSED | Y | CHATHAM
SR-62366 | DROA (I/E)- XV181747- Open limit switch error | XV-18174B | 6399 | 1 | VIRAJ.PATEL | 2024-01-12 08:12 |  | 24-2078 | CLOSED | Y | CHATHAM
SR-62296 | XV-18174 Dryer A "Cyclone Exhaust Door Trouble" | XV-18174B | 6399 | 1 | DAN.ONEILL | 2024-01-10 04:35 |  |  | CANCEL | Y | CHATHAM
SR-62215 | The hydroheater for the Turbo-Tak is leaking badly. | EJ-1837 | 2563 | 1 | MANDY.YOUNG | 2024-01-08 14:07 |  | 24-1510 | CLOSED | Y | CHATHAM
SR-62210 | TR24 - Spring The Exhaust access door for CY-1826/1827 closed switch failed | XV-18174B | 6399 | 4 | JOSH.BURM | 2024-01-08 12:19 |  | 24-1502 | CLOSED | Y | CHATHAM
SR-62204 | I believe the closed switch on the CY-1826/1827 exhaust door failed | XV-18174B | 6399 | 4 | JOSH.BURM | 2024-01-08 11:49 |  |  | CANCEL | Y | CHATHAM
SR-62200 | The hydroheater for the Turbo-Tak is leaking badly. | EJ-1837 | 2563 | 1 | JOSH.BURM | 2024-01-08 10:59 |  |  | CANCEL | Y | CHATHAM
SR-61842 | DROA - Inspect dust collector plenum | DC-1834 |  | 4 | MICHAEL.JACOBSON | 2023-12-18 13:49 |  | 23-53465 | CLOSED | Y | CHATHAM
SR-61841 | DROA - BL-1829 inspect aluminum air seal rings | BL-1829 |  | 1 | MANDY.YOUNG | 2023-12-18 13:22 |  | 23-53461 | CLOSED | Y | CHATHAM
SR-61839 | DROA - I/E - Dryer A Shutdown Clean FT18111 and FT18110 | FT-18111 | 3612 | 1 | VIRAJ.PATEL | 2023-12-18 13:13 |  | 23-53462 | CLOSED | Y | CHATHAM
SR-61256 | RV 1834 motor replace | RV-1834 |  | 1 | DEREK.WILKEN | 2023-11-22 08:55 |  | 23-51504 | CLOSED | Y | CHATHAM
SR-60812 | Ensure insulation and air hammer cables are secure DC-1834 | DC-1834 |  | 4 | MICHAEL.JACOBSON | 2023-11-06 11:25 |  | 23-50204 | CLOSED | Y | CHATHAM
SR-60810 | DROA - Replace Vent Door Gaskets | XV-18174A | 6891 | 4 | MICHAEL.JACOBSON | 2023-11-06 11:20 |  | 23-50201 | CLOSED | Y | CHATHAM
SR-60771 | P1837 Recirculation pump leaking bad | P-1837 |  | 4 | RICK.GIROUX | 2023-11-03 13:49 |  |  | CANCEL | Y | CHATHAM
SR-60760 | DC-1834 Blockage or Debris | DC-1834 |  | 1 | CHRIS.DYCK | 2023-11-03 05:07 |  | 23-49806 | CLOSED | Y | CHATHAM
SR-60674 | Repair cladding on CV-1828 | CV-1828 |  | 4 | BRAD.TINLINE | 2023-10-30 09:54 |  | 23-49728 | CLOSED | Y | CHATHAM
SR-60672 | Repair/modify scaffold at CV1828 | CV-1828 |  | 1 | BRAD.TINLINE | 2023-10-30 09:45 |  | 23-49727 | CLOSED | Y | CHATHAM
SR-60668 | DROA - P1837 recirculation pump Leaking heavily | P-1837 |  | 4 | RICK.GIROUX | 2023-10-30 02:09 |  |  | CANCEL | Y | CHATHAM
SR-60529 | Complete blower blade cleaning | BL-1829 |  | 1 | JAMMIE.DUQUETTE | 2023-10-23 11:17 |  | 23-49399 | CLOSED | Y | CHATHAM
SR-60300 | Viraj- Review Delay high AMP on RV1834 | RV-1834 | 3060 | 4 | MOHAMMED.MOUSA | 2023-10-11 15:57 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-59810 | PT18140 will need to be pulled and cleaned | PT-18140 | 3637 | 4 | DEREK.WILKEN | 2023-09-17 23:26 |  | 23-47471 | CLOSED | Y | CHATHAM
SR-59729 | PT18140 high alarm trip - not showing alarm | PT-18140 | 3637 | 4 | MOHAMMED.MOUSA | 2023-09-12 12:03 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-59607 | ATTN: I/E - CY1826 XY18174 OPEN Limit Switch Error | XV-18174A | 6891 | 1 | VIRAJ.PATEL | 2023-09-05 14:46 |  | 23-46743 | CLOSED | Y | CHATHAM
SR-58740 | Review Level switch vs timer/rake AMP | E-1834 | 2561 | 1 | MOHAMMED.MOUSA | 2023-07-18 11:25 | VIRAJ.PATEL |  | CANCEL | Y | CHATHAM
SR-58321 | Troubleshoot CV-1828 dumping to pad | CV-1828 |  | 4 | MANDY.YOUNG | 2023-06-21 07:32 |  | 23-42207 | CLOSED | Y | CHATHAM
SR-57613 | TA2024 Change out next 25 cages to SS on DC-1834 | DC-1834 |  | 4 | JAMMIE.DUQUETTE | 2023-05-17 14:16 |  | 23-39983 | CLOSED | Y | CHATHAM
SR-57499 | Verify no solids build up on the flow meter | FT-18110 | 3611 | 1 | MOHAMMED.MOUSA | 2023-05-12 11:52 |  | 23-39296 | CLOSED | Y | CHATHAM
SR-57188 | BL-1829 South Door install insulation. | BL-1829 | 10034 | 4 | MANDY.YOUNG | 2023-04-27 10:34 |  | 23-38518 | CLOSED | Y | CHATHAM
SR-56756 | DRYER A SD, I/E, HART parameters from FIT18110/1 | FT-18110 | 3611 | 1 | VIRAJ.PATEL | 2023-04-06 12:38 |  | 23-37529 | CLOSED | Y | CHATHAM
SR-56678 | Output signal on LT41310 probe | LT-41310 | 3686 | 4 | PATRICIA.HAYWARD | 2023-04-01 22:29 |  | 23-37106 | CLOSED | Y | CHATHAM
SR-56671 | Replace all Solenoid Valves on DC-1834 | DC-1834 |  | 4 | MICHAEL.JACOBSON | 2023-04-01 14:02 |  | 23-37105 | CLOSED | Y | CHATHAM
SR-56535 | Swap out Non DE Bearing in BL-1829 | BL-1829 |  | 4 | AARON.HUNTER | 2023-03-24 11:11 |  | 23-36752 | CLOSED | Y | CHATHAM
SR-56369 | BL-1829 HPW and bearings High vibrations noted | BL-1829 |  | 1 | JAMMIE.DUQUETTE | 2023-03-16 08:45 |  |  | CANCEL | Y | CHATHAM
SR-56147 | Steam leak on BL-1829 | BL-1829 |  | 1 | PATRICIA.HAYWARD | 2023-03-03 20:58 |  | 23-35286 | CLOSED | Y | CHATHAM
SR-55788 | P-1837 Leak from pump | P-1837 |  | 4 | PATRICIA.HAYWARD | 2023-02-10 16:14 |  |  | CANCEL | Y | CHATHAM
SR-55773 | DC-1834 "D" blast puck leaking air. | DC-1834 | 2537 | 1 | RYAN.VINK | 2023-02-10 07:53 |  | 23-33768 | CLOSED | Y | CHATHAM
SR-55658 | Inspect PT18140 during Dryer A outage | PT-18140 | 3637 | 1 | MOHAMMED.MOUSA | 2023-02-03 09:57 |  | 23-33660 | CLOSED | Y | CHATHAM
SR-55118 | BL-1829- inspect aluminum air seal rings | BL-1829 |  | 4 | JAMMIE.DUQUETTE | 2023-01-06 14:46 |  | 23-31559 | CLOSED | Y | CHATHAM
SR-55012 | DC 1834 Air Sweep "A" came loose | DC-1834 |  | 4 | MIKE.FARRON | 2023-01-03 04:52 |  | 23-31249 | CLOSED | Y | CHATHAM
SR-54161 | Loud Motor (Dryer A product cooler) | E-1834 | 2561 | 1 | PATRICIA.HAYWARD | 2022-11-04 01:20 |  | 22-27336 | CLOSED | Y | CHATHAM
SR-53463 | TP15 Main Fan Amp setpoint change | BL-1829 | 10034 | 4 | MOHAMMED.MOUSA | 2022-09-21 12:08 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-53446 | PRV off of P1837 recirc line leaking | P-1837 |  | 1 | MIKE.FARRON | 2022-09-20 09:53 |  | 22-24903 | CLOSED | Y | CHATHAM
SR-53438 | Dust Collector Atmp damper speed adjustment | PT-18215A | 3644 | 1 | MOHAMMED.MOUSA | 2022-09-20 07:33 |  | 22-24894 | CLOSED | Y | CHATHAM
SR-53326 | Inspect and fix leaks | CV-1828 | 2523 | 1 | JORDAN.GILBERT | 2022-09-13 15:25 |  | 22-24879 | CLOSED | Y | CHATHAM
SR-53315 | Dryer A Sump pit & assosiated equipment | LT-41310 | 3686 | 1 | PATRICIA.HAYWARD | 2022-09-13 06:09 |  | 22-24389 | CLOSED | Y | CHATHAM
SR-53275 | RV-1834 chain broke (Dryer A dust collector RV) | RV-1834 | 3411 | 1 | JAMIE.LEIDL | 2022-09-09 11:12 |  | 22-23980 | CLOSED | Y | CHATHAM
SR-53235 | Adjust the cooler louver timer TP35 to 100 sec | E-1834 | 2561 | 4 | MOHAMMED.MOUSA | 2022-09-08 09:13 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-53202 | Replace housing shaft seals | BL-1829 | 10034 | 1 | JORDAN.GILBERT | 2022-09-06 16:42 |  | 22-23966 | CLOSED | Y | CHATHAM
SR-53179 | E1834 adjust louver timer from 150sec to 120 sec | E-1834 | 2561 | 4 | MOHAMMED.MOUSA | 2022-09-06 12:05 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-53164 | Dryer A Sump: Bad I/O | LT-41310 | 3686 | 1 | DAN.ONEILL | 2022-09-04 21:05 |  | 22-23973 | CLOSED | Y | CHATHAM
SR-53152 | Dryer SD Sept 14 - Bl-1829 Drill and Tap VTs | BL-1829 | 10034 | 4 | VIRAJ.PATEL | 2022-09-02 09:26 |  | 22-24865 | CLOSED | Y | CHATHAM
SR-53150 | Blower vibrations higher than maximum levels | BL-1829 | 10034 | 1 | JAMMIE.DUQUETTE | 2022-09-01 07:50 |  | 22-23700 | CLOSED | Y | CHATHAM
SR-53125 | Inspect bearings and re-pack | BL-1829 | 10034 | 4 | JORDAN.GILBERT | 2022-08-31 15:56 |  | 22-24270 | CLOSED | Y | CHATHAM
SR-53121 | P1837 motor and seal repair | P-1837 | 6660 | 1 | JAMIE.LEIDL | 2022-08-31 14:02 |  | 22-23671 | CLOSED | Y | CHATHAM
SR-53098 | P1837 seal leak, repair | P-1837 | 6660 | 4 | CHRIS.GAGNIER | 2022-08-30 15:59 |  | 22-23715 | CLOSED | Y | CHATHAM
SR-52999 | Air Line Bleed installation for the new AirSweep System on DC1834 | DC-1834 | 2537 | 1 | MOHAMMED.MOUSA | 2022-08-25 12:29 |  | 22-23370 | CANCEL | Y | CHATHAM
SR-52954 | AirSweep Commissioning Day | DC-1834 | 2537 | 4 | MOHAMMED.MOUSA | 2022-08-23 11:02 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-52952 | AirSweep Commissioning Day | DC-1834 | 2537 | 4 | MOHAMMED.MOUSA | 2022-08-23 10:56 |  |  | CANCEL | Y | CHATHAM
SR-52900 | AirSweeps (DC1834) Dryer A Commissioning Electric | DC-1834 | 2537 | 1 | MOHAMMED.MOUSA | 2022-08-19 07:47 |  | 22-23278 | CLOSED | Y | CHATHAM
SR-52788 | Dust collector outlet pressure TP14 | DC-1834 | 2537 | 4 | MOHAMMED.MOUSA | 2022-08-11 09:28 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-52770 | Adjust down the Slinger level in the cooler | E-1834 | 2561 | 4 | MOHAMMED.MOUSA | 2022-08-10 11:35 |  | 22-22366 | CLOSED | Y | CHATHAM
SR-52757 | Cyclone door overhead limit switch replacement XV-18176 | XV-18176B |  | 4 | JAMMIE.DUQUETTE | 2022-08-09 15:56 |  | 22-22359 | CLOSED | Y | CHATHAM
SR-52755 | Change the input air flow from % to actual flow unit | FT-18111 | 3612 | 4 | MOHAMMED.MOUSA | 2022-08-09 14:29 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-52754 | Change the input air flow from % to acutal flow unit | FT-18110 | 3611 | 4 | MOHAMMED.MOUSA | 2022-08-09 14:27 | VIRAJ.PATEL |  | CLOSED | Y | CHATHAM
SR-52752 | Dust collector Outlet Pressure TP change | DC-1834 | 2537 | 4 | MOHAMMED.MOUSA | 2022-08-09 13:24 | VIRAJ.PATEL | 22-22345 | CLOSED | Y | CHATHAM
SR-52732 | Clean off fresh air intake screen for E-1834 cooler. Intake is located on top of MCC-3821. | E-1834 | 2561 | 1 | DAVIN.KENDRICK | 2022-08-08 15:11 |  | 22-22307 | CLOSED | Y | CHATHAM
SR-52701 | Troubleshoot DC-1834 for change in air flow pattern | DC-1834 |  | 1 | JAMIE.LEIDL | 2022-08-05 12:50 |  | 22-21976 | CLOSED | Y | CHATHAM
SR-52682 | Investigate high DP across DC-1834 | DC-1834 |  | 1 | JAMIE.LEIDL | 2022-08-04 11:47 |  | 22-21948 | CLOSED | Y | CHATHAM
SR-52652 | Dryer A Sump LT has gone bad I.O. | LT-41310 | 3686 | 4 | DEREK.WILKEN | 2022-08-02 13:35 |  | 22-21933 | CLOSED | Y | CHATHAM
SR-52565 | Install Temporary Insulation to reduce condensation | DC-1834 |  | 1 | MICHAEL.JACOBSON | 2022-07-27 12:09 |  | 22-21613 | CLOSED | Y | CHATHAM
SR-52419 | Inspect the FLOW METER FI18110 & FI18111 | FT-18110 | 3611 | 1 | MOHAMMED.MOUSA | 2022-07-19 08:29 |  | 22-21274 | CLOSED | Y | CHATHAM
SR-52409 | Remove bags, clean and replace | DC-1834 |  | 1 | JAMMIE.DUQUETTE | 2022-07-18 10:35 |  | 22-21252 | CLOSED | Y | CHATHAM
SR-52408 | Add blanks to dryer a system ready for CSE tomorrow | DC-1834 |  | 1 | JAMMIE.DUQUETTE | 2022-07-18 10:29 |  | 22-21251 | CLOSED | Y | CHATHAM
SR-52399 | Bag found when clearing out DC1834 | DC-1834 |  | 1 | JAMIE.LEIDL | 2022-07-16 15:45 |  | 22-21233 | CLOSED | Y | CHATHAM
SR-52345 | Dye test the dented access door to ensure no cracks. | DC-1834 |  | 4 | JAMMIE.DUQUETTE | 2022-07-12 11:34 |  | 22-20901 | CLOSED | Y | CHATHAM
SR-52330 | Guiding Bolts need backing off | BL-1829 | 10034 | 4 | VIRAJ.PATEL | 2022-07-11 11:11 |  | 22-20879 | CLOSED | Y | CHATHAM
SR-52213 | Vibration Monitoring for BL1829/25 Training | BL-1829 | 2868 | 4 | VIRAJ.PATEL | 2022-06-30 13:25 |  | 22-20536 | CLOSED | Y | CHATHAM
SR-52188 | Add second inspection/cleaning door | BL-1829 |  | 4 | JORDAN.GILBERT | 2022-06-28 17:47 |  | 22-20282 | CLOSED | Y | CHATHAM
SR-52008 | New cages are needed | DC-1834 | 2537 | 4 | JAMMIE.DUQUETTE | 2022-06-17 07:52 |  | 22-19763 | CLOSED | Y | CHATHAM
SR-51997 | SD22 - Sandblast and Paint DC-1834 | DC-1834 | 2537 | 4 | MICHAEL.JACOBSON | 2022-06-16 10:59 |  | 22-19379 | CLOSED | Y | CHATHAM
SR-51996 | Fabricate and install insulation blankets for DC-1834 | DC-1834 | 2537 | 4 | MICHAEL.JACOBSON | 2022-06-16 10:56 |  | 22-19383 | CLOSED | Y | CHATHAM
SR-51775 | new stuffing box assembly and shaft sleeve needed | CV-1828 | 2523 | 1 | BRAD.TINLINE | 2022-05-31 06:31 |  | 22-18736 | CLOSED | Y | CHATHAM
SR-51771 | Drive shaft should be replaced | CV-1828 | 2523 | 1 | BRAD.TINLINE | 2022-05-30 16:26 |  | 22-18737 | CLOSED | Y | CHATHAM
SR-51715 | CV-1828 head bearing needs replacing | CV-1828 |  | 1 | JAMMIE.DUQUETTE | 2022-05-26 12:40 |  | 22-18095 | CLOSED | Y | CHATHAM
SR-51239 | LT-41310 and LSHH-41310 in alarm | LT-41310 | 3686 | 1 | SIDNEY.STEWART | 2022-04-20 16:50 |  | 22-16179 | CLOSED | Y | CHATHAM
SR-51229 | Inspect bearings and coupling | BL-1829 |  | 1 | JORDAN.GILBERT | 2022-04-20 11:38 |  | 22-16162 | CLOSED | Y | CHATHAM
SR-50361 | Viraj - TP14 to be chnaged to -4.25 | DC-1834 | 2537 | 1 | MOHAMMED.MOUSA | 2022-02-17 13:33 |  | 22-12612 | CLOSED | Y | CHATHAM
SR-50359 | Viraj - Timer chnage from 60sec to 120 sec for louver cycle | E-1834 | 2561 | 1 | MOHAMMED.MOUSA | 2022-02-17 13:25 |  | 22-12617 | CLOSED | Y | CHATHAM
SR-50291 | Tail bearings noisy and loose | CV-1828 |  | 1 | JAMMIE.DUQUETTE | 2022-02-15 06:49 |  | 22-12568 | CLOSED | Y | CHATHAM
SR-48752 | 3 of the 4 Air-flow meters on Dryer A are in the wrong way | FT-18110 | 3611 | 1 | HENRY.TAEKEMA | 2021-11-15 15:48 |  | 21-29543 | CLOSED | Y | CHATHAM
SR-48637 | P-1837 Dryer A Hydro Heater Pump Seal Leak | P-1837 | 6660 | 4 | RYAN.VINK | 2021-11-10 09:40 |  | 21-29092 | CLOSED | Y | CHATHAM
SR-48320 | RV-1834 has a consistent knock in its gear box with each revolution | RV-1834 | 2876 | 1 | DEREK.WILKEN | 2021-10-20 21:35 |  | 21-27729 | CLOSED | Y | CHATHAM
SR-48035 | P-1837 Leaking water | EJ-1837 | 2563 | 4 | MIKE.FARRON | 2021-09-30 16:48 |  | 21-25974 | CLOSED | Y | CHATHAM
SR-47896 | Please send to Viraj - Change alarming of LT-41310 | LT-41310 | 3686 | 4 | JASON.VANDERNAALT | 2021-09-23 09:36 |  | 21-24918 | CLOSED | Y | CHATHAM
SR-47876 | RV not turning, investigation requires removal and replace | RV-1834 | 2876 | 1 | JAMMIE.DUQUETTE | 2021-09-21 08:02 |  | 21-24905 | CLOSED | Y | CHATHAM
SR-47865 | RV-1834 tripped on high AMPS | RV-1834 | 2876 | 1 | RYAN.VINK | 2021-09-20 05:47 |  | 21-24884 | CLOSED | Y | CHATHAM
SR-47828 | BL-1829 Ramping Issue | BL-1829 |  | 1 | JOSH.BURM | 2021-09-17 07:20 |  | 21-24894 | CLOSED | Y | CHATHAM
SR-47802 | Level controller not working | LT-41310 | 3686 | 4 | JORDAN.GILBERT | 2021-09-15 15:36 |  | 21-24594 | CLOSED | Y | CHATHAM
SR-47754 | RV-1834 chain drive is rattling - possibly contributing to trips of the RV | RV-1834 | 2876 | 4 | JASON.VANDERNAALT | 2021-09-13 10:13 |  | 21-24559 | CLOSED | Y | CHATHAM
SR-47676 | Viraj - TP15 setpoint from 515 to 532 | BL-1829 | 10034 | 1 | MOHAMMED.MOUSA | 2021-09-07 10:12 |  | 21-24286 | CLOSED | Y | CHATHAM
SR-47403 | Paint or mark-off step at DDG Cooler | E-1834 | 2561 | 1 | HENRY.TAEKEMA | 2021-08-17 14:34 |  | 21-23015 | CLOSED | Y | CHATHAM
SR-46990 | 1829 Blower - daily insopection | BL-1829 | 10034 | 1 | MOHAMMED.MOUSA | 2021-07-19 09:56 |  | 21-21639 | CLOSED | Y | CHATHAM
SR-46915 | Maximum limit for AMP and FLA for BL1829 Inestigation | BL-1829 | 10034 | 4 | MOHAMMED.MOUSA | 2021-07-13 12:27 |  | 21-21261 | CLOSED | Y | CHATHAM
SR-46601 | Vibration System Ethernet Connection and AI wiring | BL-1829 | 2868 | 4 | VIRAJ.PATEL | 2021-06-21 10:41 |  | 21-20049 | CLOSED | Y | CHATHAM
SR-46192 | Replace the limit switch on XV-18224 | E-1834 | 2561 | 1 | HENRY.TAEKEMA | 2021-05-25 13:04 |  | 21-18416 | CLOSED | Y | CHATHAM